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Building Department 

70 N 1st street, Campbell CA 95008

408-866-2130
Whole house rewire requirements

1. Provide cover page to clearly indicate scope of repairs to this bldg.
2. Provide information on plan to indicate where sheetrock is being removed for this remodel. Indicate R-13 insulation at exterior walls, R-30 at ceiling.

3. Provide plans that show all new electrical switching/outlet locations. Darken these locations to provide a clear/legible floor plan. At no point along the wall shall be more that 6’ from an outlet. 

4. Provide arc fault circuit breakers for all circuits except kitchen, garage and bathrooms. CEC 210-12(B)
5. Show all outlets/switching at kitchen floor plan. Indicate outlet locations so that no space along the countertop is more than 24” from and outlet. CEC 210-52(C)(1)

6. Indicate GFI protection for all countertop outlets. CEC 210-8(A)(6)

7. Provide 2-20A small appliance circuits at kitchen. Provide dedicated circuits for microwave, garbage disposal and dishwasher locations. CEC 210-11 (C)(1)
8. Provide dedicated 20A circuit for bathroom outlet locations. Show outlets and GFI protection on plan. CEC 210-8

9. Provide outlet at hallway. CEC 210-52(H)

10. Indicate all outlets to be tamperproof. CEC 406.12

11. Indicate amperage of sub panel to be installed. Provide conductor size. CEC 310-16

12. Provide lighting outlet or ½ hot outlets at all bedroom locations. CEC 210-70(A)(1)

13. Show exterior lighting and switching devices at all exterior door locations. CEC 210-70.2(b)

14. Provide exhaust fan at each bathroom locations. CBC 907.2.11.2

15. Provide mechanical exhaust to outside air at range hood locations. Title 24- 4.6.4

16. Provide hard wired smoke detectors (inner-connected) at hallways and bedroom locations. CBC 907.2.11.2

17. Provide hard wired carbon monoxide detectors at hallway and every floor level (including finished basement). CBC 420.4
